## Cover Page
SPECIFICATIONS AND BILL OF QUANTITIES WITH ENGINEERING ESTIMATE
PROJECT:
SIHUL SHIRE NICU RENOVATION
LOCATION:
SHIRE, ETHIOPIA
OWNER:
DOCTORS WITH AFRICA- CUAMM
Prepared by:- Solomon Tesfay
2024-08-20

## preamble to BOQ
Preamble to the Bill of Quantities
1. The Bill of Quantities shall be read in conjunction with the Drawings and Technical Specifications.
2. The Bill of Quantities contains the following part Bills and Schedules:
a. Bill No. 1 – Sihul Shire NICU Renovation
3. The Quantities given in the Bill of Quantities are estimated and provisional, and are given to provide a common basis for bidding. The estimated contract quantity of each item of works will be set at the time of contract signing. In addition to this the basis of payment will be the actual quantities of work ordered and carried out, as measured by the Contractor and verified by the Engineer and valued at the rates and prices bid in the priced Bill of Quantities, where applicable, and otherwise at such rates and prices as the Engineer may fix within the terms of the Contract.
4. The rates and prices bid in the priced Bill of Quantities shall, except insofar as it is otherwise provided under the Contract, include all Constructional Plant, Labor, supervision, materials, erection, maintenance, insurance, profit, taxes, and duties, together with all general risks, liabilities, and obligations set out or implied in the Contract.
5. A rate or price shall be entered against each item in the priced Bill of Quantities, whether quantities are stated or not. The cost of Items against which the Contractor has failed to enter a rate or price shall be deemed to be covered by other rates and prices entered in the Bill of Quantities.
6. The rates in this Bill of quantities shall consider all incidental works required to protect existing structures.
7. Items associated with a priced item necessary for its satisfactory fixing shall be considered as included in the rate of the item.
8. The rates given for Provisional Quantities (PQ) will be binding if the client decides to incorporate these works as additional works.
9. The whole cost of complying with the provisions of the Contract shall be included in the Items provided in the priced Bill of Quantities, and where no Items are provided, the cost shall be deemed to be distributed among the rates and prices entered for the related Items of Work.
10. The Overhead & risk and the gross profit for variation orders will be 35% .
11. General directions and descriptions of work and materials are not necessarily repeated nor summarized in the Bill of Quantities. References to the relevant sections of the contract documentation shall be made before entering prices against each item in the priced Bill of Quantities.
12. The method of measurement of completed work for payment shall be in accordance with Standard Methods of Measurement ECPN-4.
13. The Bill of Quantities contains items
a. Supplied and installed by the Prime contractor
b. Provisional Quantities Supplied and installed by the Prime contractor
c. Provisional Sum Items supplied by the Client and installed by the Prime Contractor
d. Provisional Sum Items Supplied and installed by Nominated Sub-contractor
14. Provisional Sums included and so designated in the Bill of Quantities shall be expended in whole or in part at the direction and discretion of the Engineer.
15. The duties and responsibilities of the Prime Contractor for items 13(b), 13(c) and 13 (d) above are deemed to be covered by the Contractor’s charge indicated in here. The duties and responsibilities of the Prime Contractor in addition to those indicated in the Bill of Quantities are:-
a. Handle and store materials at site both for prime contractor, the Client and nominated sub-contractor works.
b. Provide utilities like power, water and other necessary utilities for use by the Client and nominated sub-contractors.
c. Provide within the site transport and lifting equipment for all loading and unloading purposes and all required transportation within the site as required by the Client and nominated sub-contractors.
d. Provide scaffolding, ladder, etc as needed
e. Execute any incidental works, like concrete work, earthwork, finishing, patching, and chiseling as required by the Client and nominated sub- contractors.
f. Removal of debris and clean the site at completion
16. Errors will be corrected by the Employer for any arithmetic errors in computation or summation as follows:
(a) where there is discrepancy between amounts in figures and in words, the amount in words will govern
(b) where there is a discrepancy between the unit rate and the total amount derived from the multiplication of the unit price and the quantity, the unit rate as quoted will govern.
17. Rock is defined as all materials which, in the opinion of the Engineer, require blasting, or the use of metal wedges and sledgehammers, or the use of compressed air drilling for their removal, and which cannot be extracted by ripping with a tractor of at least 150 brake hp with a single, rear-mounted, heavy-duty ripper.
18. A type of bonding agent used for bonding old concrete to newly fresh one should get approval before application and the cost in connection with the bonding old concrete to newly fresh one shall be born by the Contractor.
19. All provision for sanitary pipe passage, Electrical and Sanitary ducts and provision of sleeves will have to be done during concrete works as per the Electrical and Sanitary drawings and they are deemed to be included in the other rates and prices entered in the Bill of Quantities.
20. The Contractor is responsible for the detail assessment of the Site conditions and any measure to be taken is included in the rates.
21. The removal of Surplus excavated material shall be to an appropriate place away from the construction site. The contractor shall also make arrangement to damp this surplus excavated material to the owner place by the Direction of the Resident Engineer.
22. The Contractor shall submit catalogues with full description for Items under all Divisions which include, but are not limited to: Finishing Materials, Electrical, Sanitary fittings & Equipments and shall get approval by the Engineer before purchasing or ordering.
23. All Electrical and Sanitary works /installation/ shall be done by experienced staff or specialized sub-contractor or personnel who have a minimum of eight years experience with similar works & this has to be approved by the Engineer based on their CVs & educational background and certification and recommendation and/or supervision by suppliers.
24. All Electrical and Sanitary works shall be tested & commissioned prior to filling chiseled cavities, installing ceilings, covering vertical & horizontal ducts & back filling trenches. The Contractor shall be fully responsible for all systems.
25. The Prime contractor shall submit samples of all finishing materials installed by himself and by nominated sub-contractors for approval by the Engineer and the Employer.

## Summary
SUMMARY OF PRICES
01. DEMOLITION WORK | Birr | 0
02. CONCRETE WORK | Birr | 0
03. MASONRY and BLOCKWORK | Birr | 0
04. ROOFING | Birr | 0
05. CARPENTERY AND JOINERY | Birr | 0
06. METAL WORKS | Birr | 0
07. WALL AND FLOOR FINISHING | Birr | 0
08. PAINTING | Birr | 0
09. ELECTRICAL WORK | Birr | 0
10. SANITARY WORK | Birr | 0
11. MECHANICAL WORK | Birr | 0
SERVICE SUM | Birr | 0
15% VAT | Birr | 0
GRAND TOTAL | Birr | 0
2660
|  |  | 60 | 28500
60

## BOQ
BILL OF QUANTITY - Sihul Shire Hospital NICU Renovation
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | QUANTITY
01 | DEMOLISHING WORKS
The contractor is responsible for covering any costs incurred due to damage of utility lines and care shall be taken for all existing utilities that could be covered or exposed to view throughout the project execution period.
1.1 | DEMOLISHING WORKS OF DIFFERENT STRUCTURES
Price shall include clearing the working area and disposing the debris to an appropriate location as per the Supervisor's indication.
1.1.1 | Demolish Existing walls | m2 | 64.6 |  | 0
1.1.2 | Dismantle Chipwood Ceiling | m2 | 269.1875 |  | 0
1.1.3 | Dismantle wooden doors from the walls | m2 | 15.015 |  | 0
1.1.4 | Dismantle metal doors from the walls | m2 | 20.82 |  | 0
1.1.5 | Dismantle Aluminum Curtain walls [CONTROL ROOM] | m2 | 20.125 |  | 0
1.1.6 | Dismantle metal windows from the walls | m2 | 11 |  | 0
01 | SUB TOTAL DEMOLITION WORK ETH BIRR |  |  |  | 0
02 | CONCRETE WORKS
2.1 | Cast in Place Concrete
Cast in place concrete is concrete premixed at a batching plant and transported to the work site or concrete whose ingredients are transported to the site and mixed just before casting in place. Provide cement, aggregate, water admixture, labor equipment and tools for cast in place concrete as required for the satisfactory installation of the works. Quality Assurance 031 Standards Comply with the following standards. ES C. D5 201General Requirement, Portland cement, ES C. D8 490Methods of Sampling and testing Portland cement, ESI ES C. D3 201Normal Concrete aggregate, ESI ASTM C260 Air-entraining admixtures, ASTM C494 Water-reducing, retarding and accelerating admixtures. ASTM C94Mixing water for concrete. ASTM C330 Light weight aggregate for structural concrete
2.1.1 | 50mm thick C-5 lean concrete with minimum cement content of 150kg/m3 of concrete under
2.1.1.1 | Under Corridor (Connecting to Gynecology) | m2 | 14 |  | 0
2.1.1.2 | Under Ground Floor (Oxygen Shed) | m2 | 3.6 |  | 0
2.1.2 | REINFORCED CONCRETE
2.1.2.1 | REINFORCED CONCRETE GRADE C-25 (25 MPa) cast into formworks and vibrated around rod reinforcement bars. NB: Form work and reinforcement steel will measured elsewhere.
2.1.2.1.1 | 10cm Slab for Corridor connecting to Gynecology | m² | 14 |  | 0
2.1.2.1.2 | 10 cm Ground Floor Slab for Oxygen Shed | m2 | 3.6 |  | 0
2.1.2.2 | REINFORCEMENT BARS
| Reinforcement work shall be understood as the supply and fixing of reinforcement bars, including ties and chairs. The steel bars shall be high tensile (Grade S-420) hot rolled deformed Reinforcement Steel bar |  |  |  | 0
2.1.2.2.1 | Rebar Diameter 8mm | kg | 63.2 |  | 0
02 | SUB TOTAL CONCRETE WORK ETH BIRR |  |  |  | 0
03 | MASONRY and BLOCKWORK
3.1 | HOLLOW & SOLID CONCRETE BLOCKS
3.1.1 | Hollow block - (CLASS B, Average strength of 6 Blocks 35kg/cm2, Minimum strength of Individual Block 32kg/cm2
3.1.1.1 | 200mm thick class 'B' H.C.B wall bedded and jointed in cement mortar (1:3) both side left for appropriate finishing. | m² | 40.105 |  | 0
3.1.1.2 | 150mm thick class 'B' H.C.B wall bedded and jointed in cement mortar (1:3) both side left for appropriate finishing. | m² | 29.55 |  | 0
3.1.1.3 | 40cm thick Dressed Stone Masonry Wall (one side Well Dressed) | m² | 22 |  | 0
03 | SUB TOTAL MASONRY WORK ETH BIRR |  |  |  | 0
04 | ROOF WORK
4.1 | Supply and fix roof cover in precoated or galvanized EGA 400,0.4mm thick fixed to steel lattice purlin. Price shall include ridge cap, Dia 6mm fixing J-bolts and water proof washers.(purlin measured in horizontal projection) | m² | 80.7562 |  | 0
4.2 | Supply and fix G-28 galvanized flat metal sheet gutter as per the detail drawing. price shall include all the necessary accessories, metal bracket, one coats of antirust. Development length =100cm | ml | 36.5 |  | 0
4.3 | Providing, laying and jointing of G-28 Galvanized steel circular down pipes complete with all the necessary fittings. Outer diameter Dia. 150 mm | ml | 15 |  | 0
04 | SUB TOTAL ROOF WORK ETH BIRR |  |  |  | 0
05 | CARPENTRY & JOINERY
5.1 | Carpentry and Ceiling Works
5.1.1 | Supply and fix 9mm thick high quality laminated PVC ceiling with all its accessories as per the Engineer's approval in parts of the verandah and in all rooms. The ceiling color and material type shall be approved by the engineer. | m² | 283.1875 |  | 0
5.2 | Wooden Truss and Purlin |  |  |  | 0
| Supply and fix wooden truss and purlin for the 1.2x3m Oxygen Shed All structural members shall be free of harmful defects and painted with anti termite solutions. Each truss shall be firmly fixed with the beam by a 6mm plain bar. |  |  |  | 0
5.2.1 | Upper & lower chord size-diameter 10 - 12 cm | ml | 16 |  | 0
5.2.2 | Diagonal & vertical Members size-diameter 8 - 10 cm | ml | 8 |  | 0
5.2.3 | Zigba Purlin size 5x7cm | ml | 9 |  | 0
05 | SUB TOTAL CARPENTRY AND JOINERY WORK ETH BIRR |  |  |  | 0
06 | METAL WORK
6.1 | Aluminum doors
Aluminum doors made of 1.6 mm thick extruded profiles. The aluminum profiles shall be of approved color with brushed finish cuts. Manufacturing of the doors is subject to the approval of shop drawings to be provided by the Contractor. Price shall include 6mm thick clear glass, approved type of locks, door stopper and handle. Hinges, Locks, Profiles and all important accessories should be approved by the Engineer.
Standards Comply with the following standard. Hot dip galvanized coating on iron and steel articles BS 729 Anodic oxidation coating on Aluminum BS 1615 Anodic oxide coating on Aluminum for external architectural application BS 3987 Wrought steel for mechanical & allied engineering purposes BS 970
6.1.1 | Aluminum door size 120*210cm [NEW KMC] | No | 1 |  | 0
6.1.2 | Aluminum door size 100*210cm [CRITICAL ROOM] | No | 1 |  | 0
6.1.3 | Aluminum door size 100*210cm [NEW SEPTIC ROOM] | No | 1 |  | 0
6.1.4 | Aluminum door size 255*260cm [ACCESS TO NICU] | No | 2 |  | 0
6.1.5 | Aluminum door size 295*260cm [MAIN CORRIDOR] | No | 1 |  | 0
6.1.6 | Aluminum door size 120*210cm [TRIAGE] | No | 1 |  | 0
6.1.7 | Aluminum door size 90*210cm [MOTHER'S WC] | No | 1 |  | 0
6.1.8 | Aluminum door size 80*210cm [STORE] | No | 1 |  | 0
6.1.9 | Aluminum partition, length 1195 and height 210cm with 5 doors [MOTHER'S WC] | No | 1 |  | 0
6.1.10 | Aluminum door size 70*210cm [TOILET] | No | 1 |  | 0
6.1.11 | Aluminum door size 80*210cm [STAFF ROOM, BREASTFEEDING & STERILIZATION] | No | 3 |  | 0
6.1.12 | Aluminum door size 120*210cm [OFFICE] | No | 1 |  | 0
6.1.13 | Aluminum door size 70*210cm [HANDWASH ROOM] | No | 1 |  | 0
6.2 | Aluminum Windows
| Aluminum windows made of 1.6 mm thick extruded profiles. The aluminum profiles shall be of approved color with brushed finish cuts. Manufacturing of the windows is subject to the approval of shop drawings to be provided by the Contractor. Price shall include 6mm thick clear glass, approved type of locks and handle. Hinges, Locks, Profiles and all important accessories should be approved by the Engineer. |  |  |  | 0
6.2.1 | Windows: W=150cm H=200cm [NEW SEPTIC ROOM] | No | 2 |  | 0
6.3 | LTZ Windows
| Metal windows shall be manufactured from 38X1mm LTZ frame profile and should be 1.5 mm thick. Unit price shall include: two coats of anti rust and three coats of synthetic enamel paint, 6mm thick nonreflective tinted glass, approved quality cylindrical lock, hinges, handle and any other accessories to complete the work. |  |  |  | 0
6.3.1 | Windows: W=150cm H=150cm [TRIAGE] | No | 1 |  | 0
6.3.2 | Windows: W=240cm H=60cm [MOTHER'S WC] | No | 1 |  | 0
6.3.3 | Windows: W=150cm H=150cm [TOILET] | No | 1 |  | 0
6.3.4 | Windows: W=150cm H=150cm [STERILIZATION] | No | 1 |  | 0
6.4 | Oxygen Shed
6.4.1 | Supply and fix 1.5m high Metal Structure for 1.2m x 3m Oxygen Shed with 2.5mm thick galvanized wire mesh having 50x50mm spacing and fixed to 40*40*3mm RHS post at 1m and 40*40*3mm two horizontal RHS members . Price shall include two coats of anti rust and three coats of synthetic enamel paint | ml | 4.4 |  | 0
6.4.2 | Supply and fix 1000x2000m Metal door manufactured from 38X1mm LTZ frame profile and 0.8 mm thick ribbed sheet. Unit price shall include: two coats of anti rust and three coats of synthetic enamel paint, approved quality cylindrical lock, hinges, handle and any other accessories to complete the work. | pcs | 1 |  | 0
6.5 | Aluminum Curtain Wall
6.5.1 | Dismantle and Relocate CONTROL ROOM Aluminum Curtain Wall as per the Architectural Drawings. Price shall include two coats of special aluminum paint. Color to be approved by the Architect/Engineer. | m² | 17.25 |  | 0
06 | SUB TOTAL METAL WORK ETH BIRR |  |  |  | 0
07 | WALL AND FLOOR FINISHINGS
7.1 | PLASTERING & POINTING
Finishing work includes all surface pre cleaning, removal of mortar by chiseling, making good edges of columns and beams, preparation of grooves b/n surface where ever indicated, preparation and application of finish, polishing and cleaning after end of work.
7.1.1 | Cement Mortar Plastering to internal wall. plaster shall be applied in two coats of mortar with the following ratio: First coat: 1 Part cement to 2.5 parts aggregate by volume. Second Coat: 1 Part of cement to 3 parts of aggregate by volume. The work includes chiseling for vertical concrete wall, columns and vertical beams. | m2 | 148.11 |  | 0
7.1.2 | Gypsum Plaster to internal wall: Plaster shall be applied in one coat of 3mm thick gypsum : The final fine coat gypsum plaster to be applied by trowel shall consist of one part of gypsum to three parts of lime putty, applied to a thickness of 3mm. The plaster shall be finished truly level and smooth. The plaster shall be allowed to cure. No finish shall be applied to gypsum plaster before the age of 28 days. | m2 | 148.11 |  | 0
7.1.3 | Cement Mortar Plaster to External wall: Plaster shall be applied in three coats of mortar with a ratio of 1:3. [along NEW external Windows] The final coat of cement plaster to be applied on two coat plaster shall consist of one part of cement to two parts of fine aggregate complying to BS 1199 by volume applied by trowel to a maximum thickness of 3mm. The surface shall be finished truly level and smooth. This coat shall be cured by watering for a minimum of seven days and allowed to cure for at least 28 days before further finish is applied on it. | m2 | 8.55 |  | 0
7.2 | Wall and floor finish
7.2.1 | Supply and fix 600X600X10mm Porcelain floor tiles of approved sizes and quality with cement mortar backing and joints grouted in colored cement. Pattern, color and quality shall be approved by the Engineer. | m2 | 204.3875 |  | 0
7.2.2 | Supply and fix 300X300X8mm Nonslippery Ceramic floor tiles of approved sizes and quality with cement mortar backing and joints grouted in colored cement. Pattern, color and quality shall be approved by the Engineer. [TOILETS] | m2 | 20.575 |  | 0
7.2.3 | 100x10mm Porcelain Skirting stuck to wall with cement mortar (1:3)mix. | Lm | 193.35 |  | 0
7.2.4 | Supply and fix 200x200x6mm white glazed Ceramic wall tiles with cement mortar ratio 1:2). Price shall include grouting with matching color and other necessary works. [MOTHER'S WC & SHOWERS and TOILET] | m2 | 50.49 |  | 0
7.2.5 | Supply and fix 250x750x8mm Ceramic wall tiles with adhesive powder upto a height of 1.80m. Price shall include all necessary works. [CRITICAL ROOM, SEPTIC ROOM and MAIN CORRIDOR] | m2 | 112.8 |  | 0
7.2.6 | 5cm Cement Screed Flooring for Corridor connecting to Gynecology | m2 | 14 |  | 0
7.2.7 | 280x30mm throated and weathered Granite door and window sill bedded in cement mortar (1:3) mix. It shall be chamfered at the edge, provide water drip at bottom face of sill and 2% slope towards outside. All according to the Engineer's approval. | Lm | 21 |  | 0
07 | SUB TOTAL FINISHING WORK ETH BIRR |  |  |  | 0
08 | PAINTING
8.1 | Supply and Apply three coats of Acrylic Emulsion paint to internal plastered wall surfaces. Cost includes clean both surfaces and fix all cracks with Masonry Filler. Color to be approved by the Architect/Engineer. | m2 | 465.91 |  | 0
8.2 | Supply and Apply Varnish Paint on External rendered wall surface | m2 | 168.224 |  | 0
8.3 | Supply and Apply Quartz Paint to External Wall Surface | m2 | 48 |  | 0
8.4 | Supply and Apply Quartz Paint to Oxygen Shed | m2 | 8.8 |  | 0
8.5 | Supply and Apply two coats of anti rust and three coats of synthetic enamel paint | m2 | 25.6 |  | 0
8.5.1 | Metal Structure along the Corridor connecting the two blocks | m2 | 25.6 |  | 0
8.5.2 | Existing LTZ Windows | m2 | 26.25 |  | 0
08 | SUB TOTAL PAINTING WORK ETH BIRR |  |  |  | 0
09 | ELECTRICAL INSTALLATION
Supply, Install and Test all Electrical Systems: Power Distribution Boards with Circuit Breakers, Light Fittings with Lamps, Switches, Outlets and Others including required items and accessories. All items shall be Industry standard and approved equivalent types.
9.1 | Switch Board
9.1.1 | Surface mounted Distribution Board of metal enclosure MDB-UPS with lockable door, complete with bus terminals 50A/3ph, neutral and earth bars consisting of:-
1pc main MCB of 40A/3ph
1pc RCD of 30mA/4 pole
3 pcs MCB of 16A/1ph
8 pcs MCB of 20A/1ph
2 pcs MCB of 25A/3ph
| Including 25% reserve pitches | No | 1 |  | 0
9.2 | Extra Over Light Points for Switches
9.2.1 | Flush mounted Single switch points fed through PVC insulated conductors of 3x2.5mm2 inside PVC conduits of 16mm diameter, including junction boxes | No | 16 |  | 0
9.3 | Light Points
| Flush mounted light points fed through PVC insulated conductors of 3x2.5mm2 inside PVC conduits of 16mm diameter, including junction boxes with covers and insulating screw cap connectors. |  |  |  | 0
9.3.1 | Kangaroo Mother Care Unit | No | 6 |  | 0
9.3.2 | Critical Room | No | 6 |  | 0
9.3.3 | Septic Room | No | 3 |  | 0
9.3.4 | Main Corridor | No | 5 |  | 0
9.3.5 | Triage | No | 1 |  | 0
9.3.6 | Mother's WC & Shower | No | 2 |  | 0
9.3.7 | Staff Room | No | 2 |  | 0
9.3.8 | Sterilization | No | 1 |  | 0
9.3.9 | Office | No | 1 |  | 0
9.3.10 | Store | No | 1 |  | 0
9.3.11 | Toilet | No | 1 |  | 0
9.3.12 | Breastfeeding | No | 1 |  | 0
9.3.13 | Handwash | No | 1 |  | 0
9.4 | Extra Over Light Points for Flush Mounted Switches
9.4.1 | Flush mounting single switch 774001+774041 | No | 14 |  | 0
9.4.2 | Flush mounting two way switch 774006+774041 | No | 2 |  | 0
9.5 | Flush Mounted Socket Outlet Points
9.5.1 | 16A/1P socket outlet points fed through PVC insulated conductors of 3x2.5mm2 inside PVC conduit of 16mm diameter including junction boxes with covers and insulating screw cap connectors.
9.5.1.1 | Kangaroo Mother Care Unit @+1.20m | No | 7 |  | 0
9.5.1.2 | Critical Room @+1.20m | No | 26 |  | 0
9.5.1.3 | Septic Room @+1.20m | No | 10 |  | 0
9.5.1.4 | Triage | No | 2 |  | 0
9.5.1.5 | Mother's WC & Shower | No | 3 |  | 0
9.5.1.6 | Staff Room | No | 4 |  | 0
9.5.1.7 | Sterilization | No | 2 |  | 0
9.5.1.8 | Office | No | 2 |  | 0
9.5.1.9 | Toilet | No | 1 |  | 0
9.5.1.10 | Breastfeeding | No | 1 |  | 0
9.5.1.11 | Handwash | No | 1 |  | 0
9.5.1.12 | Control Room | No | 2 |  | 0
9.6 | Flush Mounted Socket Outlets with Earth Contact
9.6.1 | Flush mounting socket outlet twin @+1.20m
9.6.1.1 | Kangaroo Mother Care Unit | No | 7 |  | 0
9.6.1.2 | Critical Room | No | 26 |  | 0
9.6.1.3 | Septic Room | No | 10 |  | 0
9.6.2 | Flush mounting single socket of 10A/1P |  |  |  | 0
9.6.2.1 | Triage | No | 2 |  | 0
9.6.2.2 | Mother's WC & Shower | No | 3 |  | 0
9.6.2.3 | Staff Room | No | 4 |  | 0
9.6.2.4 | Sterilization | No | 2 |  | 0
9.6.2.5 | Office | No | 2 |  | 0
9.6.2.6 | Toilet | No | 1 |  | 0
9.6.2.7 | Breastfeeding | No | 1 |  | 0
9.6.2.8 | Handwash | No | 1 |  | 0
9.6.2.9 | Control Room | No | 2 |  | 0
9.7 | Light Fittings
Supply, Connect and Test lamps and complete accessories.
9.7.1 | Panel LED 60x60 24W, 3500lm lf 30000hr 4000k |  |  |  | 0
9.7.1.1 | Kangaroo Mother Care Unit | No | 6 |  | 0
9.7.1.2 | Critical Room | No | 6 |  | 0
9.7.1.3 | Septic Room | No | 3 |  | 0
9.7.1.4 | Main Corridor | No | 5 |  | 0
9.7.1.5 | Triage | No | 1 |  | 0
9.7.1.6 | Mother's WC & Shower | No | 2 |  | 0
9.7.1.7 | Staff Room | No | 2 |  | 0
9.7.1.8 | Sterilization | No | 1 |  | 0
9.7.1.9 | Office | No | 1 |  | 0
9.7.2 | Circular Panel LED 18W, 2750lm lf 30000hr 4000k wp |  |  |  | 0
9.7.2.1 | Store | No | 1 |  | 0
9.7.2.2 | Toilet | No | 1 |  | 0
9.7.2.3 | Breastfeeding | No | 1 |  | 0
9.7.2.4 | Handwash | No | 1 |  | 0
09 | SUB TOTAL FOR ELECTRICAL WORK ETH BIRR |  |  |  | 0
10 | SANITARY WORK
All fixtures, equipments, pipes & materials which are specified below shall be subject to the Engineer's approval, based on Samples, Catalogues and/or Brochures presented by the contractor. Unit Price shall include all the necessary installation accessories and all assistance civil works there to for the proper installation and operation of the sanitary wares, pipe works and any other related sanitary works.
10.1 | SANITARY APPLIANCES INSTALLATION
10.1.1 | Supply and fix High quality Gold Dragon or equivalent brand Hand wash Basin. The fixture shall conform to BS5506-3 or equivalent institution. The mixing faucets, waste drain holes, bottle trap, waste fitting, connecting pieces, fixing, female attakini(60cm long) and supporting elements and all other accessories shall comply with relevant clauses of BS standard or equivalent institution. size:520x420mmx850 mm high | pcs | 8 |  | 0
10.1.2 | Supply and fix High quality Gold Dragon or equivalent brand press type dual flush (half and full flush) type Water closet (cistern and seat not monolithically casted). The fixture shall conform to BS5503-2 or equivalent institutions. The drain pipes and fitting, connecting pieces, fixing with female adaptor flexible pipe (60cm long) and supporting element and other accessories which complete the set shall comply with the relevant clauses of BS standards or equivalent institution. The water closet type must be horizontal type with p trap connection. | pcs | 2 |  | 0
10.1.3 | Supply and fix Turkish Type Water closet made of enameled sheet steel. The fixture shall conform to British Standard Specification. The waste fittings, connecting pieces, fixing and supporting elements and Complete with all the necessary accessories. | pcs | 3 |  | 0
10.1.4 | Supply and fix Shower units made of enameled fiber glass, complete with level controlled mixing valve, approved quality flexible shower head, p-smeel trap and with all other necessary accessories. Size:- 700 x 700 mm | pcs | 2 |  | 0
10.1.5 | Supply & fix floor drain (50mm) Chrome plated complete with P-smell trap and all necessary accessories. | pcs | 3 |  | 0
10.1.6 | Supply and fix stainless steel Sink , double bowel, complete with trap, drain connection, drainage and over flow, heavy duty mixing faucet, plug, chain, etc. and all other necessary faucet, plug, chain, etc. and all other necessary accessories. Size:- 1500 x 500 x150mm (bowl depth) | pcs | 1 |  | 0
10.2 | WATER SUPPLY SYSTEM
10.2.1 | Supply and install 5,000 liters capacity Fiber Glass water tank complete with required gate valves, Ø50mm, inlet (Ø50mm) and outlet pipe (Ø32mm), over flow (Ø40mm) & drain (Ø40mm), vent pipe and all the necessary accessories thereto. The tank shall be placed on flat surface on concrete floor on top of 70cm Masonry Wall included in the price. | pcs | 1 |  | 0
10.2.2 | Supply and install Polypropylene Random Co-polymer resins (PP Type 3 raw material) PPR PN-20 to internal cold water distribution system as shown on the drawing. Complete with all the necessary fittings and accessories. All diameters specified here are internal (Nominal) diameters. |  |  |  | 0
10.2.3 | a) Dia. 25 mm | ml | 38 |  | 0
10.2.4 | Supply and fix 15mm dia chrome plated brass quarter turn angle valves with chrome plated copper connecting pipe, union nut and chrome plated brass wall flanges, and accessories complete in all respects. The Angle valve should be capable resisting of PN-16 before hand wash basins, water closets and other fixtures. | pcs | 16 |  | 0
10.2.5 | Supply and fix PPR service valves of approved standard, capable of resisting PN-10 on internal branch and pipe inlet to toilet, bath room, etc.; | pcs | 22 |  | 0
10.3 | WASTE WATER DRAINAGE SYSTEM
| All domestic waste, vent and storm water pipe lines shall be comply to BS 459, BS 4660, BS 5481 as appropriate, using double ring seals and gaskets complying with BS 2394 uPVC, PN-6 pipes and shall be provided with a minimum slope as stated in the drawing. Pipes and necessary fittings shall be standard quality and be free from damage during storage, construction and etc. Unit price shall include all the necessary assistance civil works, such as excavation cartaway, fixing or hanging to walls, beams or slabs. etc., necessary fittings such as bends, Y, etc. Storm water uPVC, PN-6 pipes shall resist the external temperature and the quality shall meet the purpose. Flushing and testing of waste water system. Flushing has to be done to clean the pipe line from debris and silts. All waste water Pipe shall be tested by water pressure of 1.5 meters head for minimum of Four Hours. |  |  |  | 0
10.3.1 | Providing, laying and jointing of internal uPVC PN-6 waste pipes with all uPVC pipe fittings including jointing with solvent cement joints and testing of joints etc. according to where shown on the drawings. Complete with all the necessary fittings. Provide cleaning detail for all waste water riser pipes as per the detail drawing. |  |  |  | 0
| Dia. 50 mm, Outer diameter | ml | 40 |  | 0
| Dia. 110 mm, Outer diameter | ml | 20 |  | 0
| Dia. 160 mm, Outer diameter | ml | 5 |  | 0
10 | SUB TOTAL FOR SANITARY WORK ETH BIRR |  |  |  | 0
11 | MECHANICAL INSTALLATION
11.1 | Manual Oxygen Manifold (2 x 3), 500 Lt/min manufactured with the following standards and requirements: BS EN 7396-1: Pipeline Systems for Compressed Medical Gases and Vacuum. BS EN 10524-2: Pressure Regulators. BS EN 21969 High-Pressure Flexible Connectors. | pcs | 1 |  | 0
11.2 | Wall Outlet Terminals, Oxygen |  |  |  | 0
11.2.1 | Critical Room | pcs | 8 |  | 0
11.2.2 | Septic Room | pcs | 4 |  | 0
11.3 | Copper tubing, Dia.22mm | ml | 40 |  | 0
11.4 | Copper tubing, Dia.12mm | ml | 24 |  | 0
11.5 | Copper tube accessories like T, Elbow, direct, etc connectors | pcs | 40 |  | 0
11.6 | Pipe Clip, ring | pcs | 50 |  | 0
11.7 | Line Valves | pcs | 2 |  | 0
11.8 | Flow Meter with Humidifier 0-15 |  |  |  | 0
11.8.1 | Critical Room | pcs | 8 |  | 0
11.8.2 | Septic Room | pcs | 4 |  | 0
11.9 | Labor (including all welding and installation material) | set | 1 |  | 0
11 | SUB TOTAL FOR MECHANICAL WORK ETH BIRR |  |  |  | 0

## TO-1
Sihul Shire Hospital NICU Renovation
Description
DEMOLITION
Existing Walls
Control Room
1 | 1 |  | Demolish for New Door
| 2.1 | 2.1
Septic Room
2 | 1.5 |  | Demolish for 2 New Windows
| 2 | 6
Septic Room
1 | 1 |  | Demolish for New Door
| 2.1 | 2.1
Triage
1 | 1 |  | Demolish for New Window
| 2 | 2
Toilet
1 | 0.9 |  | Demolish for New Door
| 2.1 | 1.89
Demolish Wall between Triage and Toilet
1 | 4
| 3.2 | 12.8
Store
1 | 0.8 |  | Demolish for New Door
| 2.1 | 1.68
Handwashes
3 | 3.25 |  | Demolish Walls on both sides
| 3.2 | 31.2
NEW Toilet
1 | 0.7 |  | Demolish for New Door
| 2.1 | 1.47
NEW Staff Room
1 | 0.8 |  | Demolish for New Door
| 2.1 | 1.68
Breastfeeding
1 | 0.8 |  | Demolish for New Door
| 2.1 | 1.68
|  | 64.6 | m2
HCB WORK
200mm thick
Control Room
1 | 1.2 |  | Cover Existing door
| 2.1 | 2.52
NEW Septic Room
1 | 1.2 |  | Cover Existing door
| 2.1 | 2.52
Triage
1 | 4 |  | New Wall
| 3 | 12
Triage
1 | 2 |  | Cover Existing Window
| 2 | 4
Handwash
2 | 0.75 |  | Cover Existing door
| 2.1 | 3.15
Toilet
1 | 0.75 |  | Cover Existing door
| 2.1 | 1.575
Toilet
1 | 1.5 |  | Cover Existing Window
| 2 | 3
Shower
1 | 0.75 |  | Cover Existing Door
| 2.1 | 1.575
Handwash
1 | 0.65 |  | Cover Existing Door
| 2.1 | 1.365
Staff Room
1 | 2 |  | Cover Existing Window
| 2 | 4
Oxygen Shed
1 | 4.4 |  | H=1.0
| 1 | 4.4
|  | 40.105 | m2
150mm thick
Store
1 | 4.35 |  | New Partition Wall
| 3 | 13.05
Staff Room
1 | 5.5 |  | New Partition Wall
| 3 | 16.5
|  | 29.55 | m2
External wall
Triage
2 | 2 |  | Cover Existing Window
| 2 | 8
Toilet
2 | 1.5 |  | Cover Existing Window
| 2 | 6
Staff Room
2 | 2 |  | Cover Existing Window
| 2 | 8
|  | 22 | m2
PLASTERING
|  | 56.21 | Cover Existing Doors and Windows
|  | 24 | Triage New Wall
|  | 26.1 | Store New Wall
|  | 33 | Staff Room New Wall
|  | 8.8 | Oxygen Shed
|  | 148.11 | m2
PAINTING
Internal Wall
2 | 3.2
| 18.25 | 116.8 | Main Corridor
2 | 3
| 3 | 18 | Above the 2 Main doors
Deduct Openings
-3 | 1.2
| 0.3 | -1.08 | Doors 1.20x2.10 - 2 Sides
-2 | 1
| 0.3 | -0.6 | Doors 1.00x2.10 -2 Sides
-1 | 0.9
| 0.3 | -0.27 | Doors 0.90x2.10 - 2 Sides
-4 | 0.8
| 0.3 | -0.96 | Doors 0.80x2.10 -2 Sides
1 | 26.1
| 3 | 78.3 | KMC
-2 | 2
| 2 | -8 | Deduct Windows
-1 | 1.2
| 2.1 | -2.52 | Deduct Doors
1 | 26.1
| 1.2 | 31.32 | Critical Room
-2 | 2
| 1.2 | -4.8 | Deduct Windows
-2 | 1.5
| 1.2 | -3.6 | Deduct Windows
-1 | 1
| 0.3 | -0.3 | Deduct Doors
1 | 19.1
| 1.2 | 22.92 | Septic Room
-1 | 2
| 1.2 | -2.4 | Deduct Windows
-2 | 1.5
| 1.2 | -3.6 | Deduct Windows
-1 | 1
| 0.3 | -0.3 | Deduct Doors
1 | 12
| 3 | 36 | Triage
-1 | 1.5
| 1.5 | -2.25 | Deduct Windows
-1 | 1.2
| 2.1 | -2.52 | Deduct Doors
1 | 17.1
| 1.2 | 20.52 | Mother's WC
-1 | 2.4
| 0.6 | -1.44 | Deduct Windows
-1 | 0.9
| 0.3 | -0.27 | Deduct Doors
1 | 8.7
| 3 | 26.1 | Store
1 | 15.1
| 3 | 45.3 | Staff Room
-1 | 1.5
| 1.5 | -2.25 | Deduct Windows
-1 | 0.8
| 2.1 | -1.68 | Deduct Doors
1 | 7
| 1.2 | 8.4 | Toilet
-1 | 1.5
| 1.2 | -1.8 | Deduct Windows
-1 | 0.7
| 0.3 | -0.21 | Deduct Doors
1 | 6.7
| 3 | 20.1 | Breastfeeding Room
-1 | 0.8
| 2.1 | -1.68 | Deduct Doors
1 | 11.2
| 3 | 33.6 | Sterilization
-1 | 0.8
| 2.1 | -1.68 | Deduct Doors
-1 | 1.5
| 1.5 | -2.25 | Deduct Windows
1 | 14.5
| 3 | 43.5 | Office
-1 | 2
| 2 | -4 | Deduct Windows
-1 | 1.2
| 2.1 | -2.52 | Deduct Doors
1 | 6.5
| 3 | 19.5 | Handwash Room
-1 | 0.7
| 2.1 | -1.47 | Deduct Doors
|  | 465.91 | m2
FLOOR FINISH
Porcelain Tiles 600x600x10mm
1 | 18.25
| 2.95 | 53.8375 | Main Corridor
1 | 6.3
| 6.75 | 42.525 | KMC
1 | 6.3
| 6.75 | 42.525 | Critical Room
1 | 6.3
| 3.25 | 20.475 | Septic Room
1 | 4
| 2 | 8 | Triage
1 | 1
| 3.25 | 3.25 | Store
1 | 3.55
| 4 | 14.2 | Staff Room
1 | 1.85
| 1.5 | 2.775 | Breastfeeding Room
1 | 1.6
| 4 | 6.4 | Sterilization
1 | 3.25
| 4 | 10.4 | Office
204.3875
Ceramic Tiles 300x300x8mm
1 | 4.55
| 4 | 14.95 | Mother's WC and Shower
1 | 1.5
| 2 | 3 | Toilet
1 | 1.5
| 1.75 | 2.625 | Handwash
20.575
WALL FINISH
Ceramic Wall Tiles 300x300x6
1 | 17.1
| 1.8 | 30.78 | Mother's WC
-1 | 0.9
| 1.8 | -1.62 | Deduct Doors
1 | 7
| 1.8 | 12.6 | Toilet
-1 | 1.5
| 0.3 | -0.45 | Deduct Windows
-1 | 0.7
| 1.8 | -1.26 | Deduct Doors
1 | 6.5
| 1.8 | 11.7 | Handwash Room
-1 | 0.7
| 1.8 | -1.26 | Deduct Doors
50.49
Ceramic Wall Tiles 250x750x8
1 | 26.1
| 1.8 | 46.98 | Critical Room
-2 | 2
| 0.8 | -3.2 | Deduct Windows
-2 | 1.5
| 0.8 | -2.4 | Deduct Windows
-2 | 1
| 1.8 | -3.6 | Deduct Doors
1 | 19.1
| 1.8 | 34.38 | Septic Room
-1 | 2
| 0.8 | -1.6 | Deduct Windows
-2 | 1.5
| 0.8 | -2.4 | Deduct Windows
-2 | 1
| 1.8 | -3.6 | Deduct Doors
2 | 1.8
| 18.25 | 65.7 | Main Corridor
Deduct Openings
-3 | 1.2
| 1.8 | -6.48 | Doors 1.20x2.10 - 2 Sides
-2 | 1
| 1.8 | -3.6 | Doors 1.00x2.10 -2 Sides
-1 | 0.9
| 1.8 | -1.62 | Doors 0.90x2.10 - 2 Sides
-4 | 0.8
| 1.8 | -5.76 | Doors 0.80x2.10 -2 Sides
112.8
Porcelain Skirting
|  | 24.9 | KMC
|  | 25.1 | Critical Room
|  | 18.1 | Septic Room
|  | 10.8 | Triage
|  | 7.7 | Store
|  | 14.3 | Staff Room
|  | 5.9 | Breastfeeding Room
|  | 10.4 | Sterilization
|  | 16.8 | Office
|  | 20.45 | Mother's WC
|  | 6.3 | Toilet
|  | 5.8 | Handwash
|  | 26.8 | Main Corridor
193.35
Windowsill
New Windows
5 | 1.5 | 7.5
1 | 2.4 | 2.4
Doorsill
3 | 1.2 | 3.6 | 1.20 doors
2 | 1 | 2 | 1.00 doors
1 | 0.9 | 0.9 | 0.90 doors
4 | 0.8 | 3.2 | 0.80 doors
2 | 0.7 | 1.4 | 0.70 doors
|  | 21 | m

## Re-bar
No | Member | Shape | Dia | length | No of bar | No of member | Ø6 | Ø8 | Ø10 | Ø12 | Ø14 | Ø16 | Ø20 | Ø24
Corridor to Gynecology
|  |  | 8 | 4 | 15 | 1 | Ø8: 60
|  |  | 8 | 3.5 | 17 | 1 | Ø8: 59.5
Oxygen Room
|  |  | 8 | 3 | 7 | 1 | Ø8: 21
|  |  | 8 | 1.5 | 13 | 1 | Ø8: 19.5
|  |  | total length (m) |  |  |  | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | weight per meter(Kg/m) |  |  |  | 0.222 | 0.395 | 0.617 | 0.888 | 1.208 | 1.578 | 2.466 | 3.551
|  |  | total weight (kg) |  |  |  | 0 | 63.2 | 0 | 0 | 0 | 0 | 0 | 0

## Rebar (hidden)
| 8 | 10 | 12 | 14 | 16 | 20 | 24
Bm 3 | 246.4385 |  |  | 124.1
BM 2 | 120.3577 |  |  | 72.1
| 278.6538 |  |  | 135.18
Bm A | 63.8077 |  |  | 28.2
BM B | 128.6538 |  |  | 67.8
BM C | 128.0769 |  |  | 68.4
BM D | 128.0769 |  |  | 83.6
MB H | 200.7692 |  |  | 94.9
BM F | 122.3077 |  |  | 55.9
| 39.2308 |  |  | 25.85
BM E | 115.3846 |  |  | 63.7
BM G | 167.3077 |  |  |  | 53.8 | 123.2
BM 1 | 159.2308 |  |  | 33.4 | 41.6
| 57.6923 |  |  | 31.7
| 123.4615 |  |  |  | 26.6 | 34.2
BM 4 | 271.1538 |  |  | 68.15 | 71.6
BM 2 | 308.0769 |  |  |  | 70.5 | 76.3
| 140.7692 |  |  | 34 | 43.1
BM 3 | 182.3077 |  |  |  | 61.4 | 59.65
BM B | 245.7692 |  |  |  | 53.2 | 63
BM C | 265.3846 |  |  |  | 12.8 | 161.6
BM D | 276.9231 |  |  |  | 63.8 | 87.9
BM E | 152.3077 |  |  |  | 41.15 | 58.4
BM G | 227.3077 |  |  |  | 56.7 | 75.5
BM F | 191.5385 |  |  |  | 42.6 | 65.6
BM H | 189.2308 |  |  |  |  | 119.7
BM 1 Arc | 121.1538 |  |  |  | 8.1 | 115.2
BM 4 arc | 211.1538 |  |  |  | 18.2 | 213.8
BM I' | 139.6154 |  |  |  | 31.8 | 39.2
at elev 3, 8, 12
BM 1 | 626.5385 |  |  |  | 161.1 | 185.4
| 491.5385 |  |  |  | 124.8 | 211.8
BM 2 | 443.0769 |  |  |  |  | 356.1
| 408.4615 |  |  |  | 101.7 | 135.9
BM 3 | 1045.3846 |  |  |  |  | 649.5
BM C | 778.8462 |  |  |  | 187.8 | 219.3
BM 4 | 1125 |  |  |  | 291.6 | 349.5
BM D | 810 |  |  |  | 190.2 | 306.6
BM G | 681.9231 |  |  |  | 174.9 | 227.1
BM H | 571.1538 |  |  |  | 117.3 | 139.5
BM E | 363.4615 |  |  | 105.6 | 106.5
BM E&F | 369.2308 |  |  |  | 150.6 | 248.4
| 242.3077 |  |  |  | 61.2 | 177.6
BM E | 138.4615 |  |  |  | 30.6 | 53.4
BM A | 461.5385 |  |  | 25.8 | 336 | 57.6
BM 1&2 Arc | 706.1538 |  |  |  | 139.2 | 812.4
BM 4 arc | 634.6154 |  |  |  | 234 | 279.6
BM I' | 272.3077 |  |  |  | 94.2 | 128.4
TYP
BM 3 | 2090.7692 |  |  |  |  | 1299
BM 2 | 886.1538 |  |  |  |  | 712.2
| 816.9231 |  |  |  | 203.4 | 271.8
BM 1 | 630 |  |  |  | 84.6 | 194.4
BM H | 1142.3077 |  |  |  | 306.6 | 411
BM D | 1107.6923 |  |  |  | 355.2 | 232.8
BM F&G | 2450.7692 |  |  |  | 168.3 | 858
BM F | 572.3077 |  |  |  | 192 | 285.6
| 184.6154 |  |  |  |  | 155.4
BM 1 Arc | 1412.3077 |  |  |  | 278.4 | 1624.8
BM 4 arc | 1278.4615 |  |  |  | 234 | 726.6
BM C&I' | 1089.2308 |  |  |  | 376.8 | 513.6
Total | 28833.6808 | 0 | 0 | 1118.38 | 5397.95 | 13116.55 | 0