## Cover Page
SPECIFICATIONS AND BILL OF QUANTITIES
PROJECT:
MEDICAL GASES SUPPLY WORKS AT TIKUR ANBESSA(BLACKLION) SPECIALIZED HOSPITAL
LOCATION:
ADDIS ABABA, ETHIOPIA
OWNER:
DOCTORS WITH AFRICA- CUAMM
2026-04-01

## SUMMARY
Tikur Anbessa Specialized Hospital Medical Gases Supply Works
ITEM |  | DESCRIPTION | Total
1.1 | Medical Air @4Bar System | MEDICAL AIR @4BAR SYSTEM | 0
1.2 | Oxygen Automatic Manifold | OXYGEN AUTOMATIC MANIFOLD | 0
1.3 | VACUUM PLANT | VACUUM PLANT | 0
1.4 | MEDICAL GAS FLOW METER for oxygen | MEDICAL GAS FLOW METER FOR OXYGEN | 0
1.5 | MEDICAL GAS FLOW METER for Medical air | MEDICAL GAS FLOW METER FOR MEDICAL AIR | 0
1.6 | MEDICAL Vacuum regulator | MEDICAL VACUUM REGULATOR | 0
1.7 | ZONE SERVICE UNITS WITH INTEGRATED AREA ALARM | ZONE SERVICE UNITS WITH INTEGRATED AREA ALARM | 0
1.8 | MASTER ALARM UNIT | MASTER ALARM UNIT | 0
1.9 | PIPE WORK | PIPE WORK | 0
1.10 | LINE VALVES | LINE VALVES | 0
1.11 | Medical Gas Terminal Units | MEDICAL GAS TERMINAL UNITS | 0
1.12 | TRUNKING | TRUNKING | 0
1.13 | OXYGEN MANIFOLD RELOCATION AND INTEGRATION WORKS | OXYGEN MANIFOLD RELOCATION AND INTEGRATION WORKS | 0
1.14 | MEDICAL AIR PLANT RELOCATION AND INTEGRATION WORKS | MEDICAL AIR PLANT RELOCATION AND INTEGRATION WORKS | 0
1.15 | MGPS PLANT ROOM LIGHTWEIGHT ACOUSTIC ENCLOSURE AND ASSOCIATED WORKS Note: This intervention subjected for prior approval and the actual location will be defined during the site visit. | MGPS PLANT ROOM LIGHTWEIGHT ACOUSTIC ENCLOSURE AND ASSOCIATED WORKS NOTE: THIS INTERVENTION SUBJECTED FOR PRIOR APPROVAL AND THE ACTUAL LOCATION WILL BE DEFINED DURING THE SITE VISIT. | 0
|  | Total | 0

## BOQ
S.NO | ITEM DESCRIPTION | UNIT | Qty | Rat | Amount
1 PIPED MEDICAL GAS SYSTEMS
1.1 | Medical Air @4Bar System
Supply, install, test and commission Medical AIR @4BAR SYSTEM oil Free continuous air system complete with Air-Drier, inlet filter, High Efficienty electrical motor and motor starter, pully, pressure reducing station, air receiver, electrical control and all required accessories with the requirment of HTM2022.
All equipment and components should comply with international medical gas standards (e.g., ISO 7396-1, EN 737-3, NFPA 99, etc.).
1 Working Conpressor set
Capacity: 2470LPM
oil free Compressor ystem
Control System: PLC with digital pressure monitoring and automatic start/stop
Features:
Silent operation (Noise level: ≤ 60 dB)
High-efficiency air filtration and cooling system
Overload and overheat protection
Air Receiver Tank
Description: Surge tank for air storage
Quantity: 1000litre
Material: Carbon steel, welded
Working Pressure: 4bar
Design Pressure: 11bar
Safety Features: Pressure relief valve,Pressure gauge,Manual drain valve,Automatic condensate drain valve,Epoxy or corrosion-resistant finish
Air Drying System
Description: Medical air dryer
Quantity: 1 unit
Type: Refrigerant type air dryer
Drying Capacity: 2470 lpm
Operating Pressure: 4bar
Dew Point: 20-30°C
Features: Built-in filters for fine particles and moisture removal Automatic drain system Pressure differential indicators Energy-efficient design
Pressure Regulators
Valves and Flow Meters
Electrical Control Panel
Description: Control panel for system monitoring and operation Voltage: 380V, 3ph,Frequency: 50Hz Control Type: PLC-based Features: Auto-start/stop based on pressure levels Compressor load sharing Alarm and warning systems for fault detection (e.g., low pressure, high pressure, high temperature) Remote monitoring capability (optional) Visual indicators (LED) for operation status Emergency stop button Dew Point Monitor
Filters
Description: Air filtration system for the surgical air plant Efficiency: ≥ 99.9% for particulate removal Features: Easy-to-replace elements Pressure differential indicator filter monitoring Set Should include:intake air fiter,Afterfilter,Fine Filter, Active carbon filter, Bacterial Filter
| Medical Air @4Bar System | set | 1 |  | 0
1.2 | Oxygen Automatic Manifold
Supply,Install and commissioning emergency stand by oxygen cylinder manifolds. The unit is supplied as a complete factory tested package.The cylinder mainfold should be as per as BS EN ISO 7396- 1:2007+A2:2010 standard.ENISO 7386 and ENISO 7396-1, ISO 10083, European Pharmacopeia HTM 02-01
The plant includes:
Auto. Change-Over Unit-150Nm3/h with 2nd Stage, 4bar, w/ Transducer, O2
Features: Automatic switching between cylinders with no manual intervention Integrated pressure and oxygen concentration monitoring Visual and audible alarms for low pressure or cylinder changeover Automatic shutoff valve when the oxygen supply from cylinders reaches a critical level Manual override capability for maintenance and emergencies High-quality stainless steel construction for durability and corrosion resistance Equipped with safety relief valves and check valves Designed for continuous operation with a high level of reliability Note: Cylinder not included
Manifold capacity 10cylinders(2x10 each side)
High Pressure Manual Evacuation Valve-O2
Panel Board,
Cylinder Hose-Ramp-Cylinders, O2
Cylinder Rack-10 Cylinders each side
| Digital Alarm | set | 1 |  | 0
1.3 | VACUUM PLANT
Supply, installation, testing and commissioning of Duplex lubricate medical raotary vaccum system with high efficiency electric motor and starter, silencer, NRV, shut off ball valve, guafes, pressure switches, bacterial filter with drainage trap, operating and indicating system, storage vessel and all required accessories with the requirment of HTM 2022 . All components comply with medical vacuum system standards (e.g., ISO 7396-1, EN 737-3, NFPA 99).
Features:
Dual system for uninterrupted vacuum supply with automatic switching Continuous 24/7 operation PLC-controlled Equipped with vacuum relief valve and check valves Anti- Bacterial Filter
Vacuum Receiver Tank
Quantity: 1 unit 500 L Material: painted steel Capacity: compatable with the pump capacity Features: Automatic condensate drainage system Pressure relief valve Equipped with vacuum and pressure gauges Corrosion-resistant finish
Vacuum Piping and Valves
Valves: Isolation valves (manual ) Check valves to prevent backflow Pressure relief valves for safety
Vacuum Gauges
Real-time vacuum monitoring Easy-to-read display Compatible with the PLC control system
Electrical Control Panel
Control Type: PLC-based with touchscreen interface
Features: Auto-start/stop for vacuum pumps based on system pressure Alarms for low vacuum or system faults Manual override and remote monitoring capability
Vacuum Relief Valve
Features: Protects the system against overpressure Automatic operation with adjustable setpoints
| capacity 700LPM each | set | 1 |  | 0
1.4 | MEDICAL GAS FLOW METER for oxygen
Supply of medical gas flow meter. The unit is supplied as a complete package, fully tested prior to shipping. The unit includes maintanance valve safety nut, check valve, flush box with base block sealing ring ,o- ring, plug -in coupling, internal and external gas identification, release bushing and cover plate.
As per specification in the attachment, including regulatory & standards: bears CE marking under MDR, lS0 13485
1.4.1 | 0-3.5L/min
Oxygen flow meters serving NICU cots shall be low-flow neonatal type, with a calibrated flow range of 0–3.5 L/min (or 0–5 L/min), suitable for 400 kPa pipeline pressure, oxygen-clean, and compliant with HTM 02-01, NFPA 99, and ISO 10524.
| Medical Oxygen Flow meter with Humidifier ( BS type ) | No | 40 |  | 0
1.4.2 | 0-15L/min (For resurraction optional)
0-15 L/min,accuracy 10%, dual taper graduations 0.5 L/min (0–5 L/min range) and 1 L/min (5 L/min – maximum range)suitable for 400 kPa pipeline pressure, oxygen-clean, and compliant with HTM 02-01, NFPA 99, and ISO 10524.
| Medical Oxygen Flow meter with Humidifier ( BS type ) | No | 10 |  | 0
1.5 | MEDICAL GAS FLOW METER for Medical air
Supply of medical gas flow meter. The unit is supplied as a complete package, fully tested prior to shipping. The unit includes maintanance valve safety nut, check valve, flush box with base block sea;omg ring ,o- ring, plug -in coupling, internal and external gas identification, release bushing and cover plate.
Medical Air flow meters serving NICU cots and clinical points shall be neonatal-suitable variable-area (Thorpe tube) type, designed for use with Medical Air at 400 kPa (MA4) pipeline pressure. Flow meters shall have a calibrated flow range of 0–15 L/min, providing adequate resolution at low flows and compatibility with neonatal devices such as CPAP systems, air–oxygen blenders, and neonatal ventilators. Flow meters shall be oxygen-clean, constructed of non-flammable and corrosion-resistant materials, and compliant with HTM 02-01, NFPA 99, and ISO 10524 requirements. Each flow meter shall incorporate a back-check valve, anti- free-flow design, and a clearly readable, permanently marked scale
Pressure Regulator for Medical Air
| Surgical Air (4bar) Flow meter ( BS type ) | No. | 40 |  | 0
1.6 | MEDICAL Vacuum regulator
Supply, installation, testing and commissioning of ward vaccum units Vacuum outlets in the NICU shall be fitted with adjustable medical–surgical vacuum regulators, suitable for connection to the central vacuum pipeline system. Regulators shall provide an adjustable vacuum range of 0 to −60 kPa (or up to −80 kPa maximum) with ﬁne control suitable for neonatal use. Each regulator shall incorporate an integral vacuum gauge graduated in kPa and/or mmHg, overflow protection, and a hydrophobic bacterial filter. Vacuum regulators shall be designed to prevent the ingress of liquids into the pipeline system and shall be compatible with disposable or reusable suction collection jars. All vacuum accessories shall comply with HTM 02-01 and NFPA 99 requirements
| Medical Vacuum Flow meter with WEST Bottle ( BS type ) | No. | 40 |  | 0
1.7 | ZONE SERVICE UNITS WITH INTEGRATED AREA ALARM
Supply, Installation, testing and commissioning of medical gas Zone service Valve unit with valves,pressure gauges and NIST connect fully comply to BS ES ISO 7396-1:2007+A2 2010
The unit is supplied as a complete package, fully tested prior to shipping. The unit equipped with stamped gas identification shut-off valve (100% leakage free) The unit shall be used for all medical gases specified on the drawing.
Note service valve unit SHOULD be integrated with area alarm in one control panel as per HTM 01 02
The module must fulfill HTM 02 01 requirements.
| 3 GASES AREA valve box (O2,VAC, Medical air) | NO | 2 |  | 0
1.8 | MASTER ALARM UNIT
Supply, Installation, testing and commisioning of medical gas Master alarm service module. The unit is supplied as a complete package, fully tested prior to shipping. The unit equipped with stamped gas identification shut-off valve (100% leakage free) stainless steel back plate, box, clear emergency glass panel, local area alarm, pressure switch, indication light, acess panel internal battery and fully integrated control. The unit shall be used for all medical gases and vacuum as shown and specified on the drawing.
| MASTER ALARM ( FOR 3GASES ) | No | 1 |  | 0
1.9 | PIPE WORK
Supply,Install oxy/med copper pipe as shown on the drawing complete with all fittings, valves,sealant,support hanger and all accessories to make the system functional. Copper tubing used for medical gas and vacuum pipeline systems (oxygen, medical air, and vacuum) shall be seamless, medical-grade copper manufactured and certified in accordance with EN 13348. Tubing shall be supplied internally degreased, dried, and free from particulate contamination, suitable for oxygen service, and capped at both ends to prevent contamination during storage and installation. Copper pipes shall be installed strictly in accordance with HTM 02-01, NFPA 99, and the manufacturer’s recommendations, including requirements for cleanliness, jointing, pressure testing, and identification.
| Copper Pipe-Med, EN13348, ø22mm | Mt | 55 |  | 0
| Copper Pipe-Med, EN13348, ø28mm | Mt | 82 |  | 0
| Copper Pipe-Med, EN13348, ø35mm | Mt | 65 |  | 0
1.1 | LINE VALVES
Supply and install Branch isolation valves serving oxygen, medical air, and vacuum pipeline branches, Valves shall be full-bore, quarter-turn ball valves specifically designed and certified for medical gas service. Valves shall be manufactured from dezincification-resistant brass or approved equivalent, be factory cleaned for oxygen service, and supplied capped to prevent contamination. Each branch isolation valve shall be fitted with a lockable operating handle to prevent inadvertent operation and shall be clearly labeled to identify the service gas and the area served. Installation of branch isolation valves shall comply with the requirements of HTM 02-01 and NFPA 99, ensuring accessibility for operation and maintenance
| Ball Valve Set, Chrome Plated, Male Conical Coupling - 28mm | No. | 5 |  | 0
| Ball Valve Set, Chrome Plated, Male Conical Coupling - 15mm | No. | 16 |  | 0
| Ball Valve Set, Chrome Plated, Male Conical Coupling - 22mm | No. | 10 |  | 0
| Ball Valve Set, Chrome Plated, Male Conical Coupling - 35mm | No. | 3 |  | 0
1.11 | Medical Gas Terminal Units
1.11.1 | Medical Gas Terminal Units with isolated arrangment
Medical gas terminal units shall be specifically designed for use in healthcare facilities and shall comply with HTM 02-01, NFPA 99, and EN ISO 7396-1 requirements. Terminal units shall be non-interchangeable between different gas services, incorporate an automatic self-sealing valve, and be suitable for the nominal pipeline operating pressure of the respective service. Terminal units shall be permanently gas-identified by color coding and clear labeling and shall be compatible with the medical gas outlet probe standard adopted for the facility
A)Oxygen Terminal Units
Supply,Installation, testing and commissioning of Oxygen terminal units shall be designed for connection to a 400 kPa medical oxygen pipeline system and shall incorporate an automatic shut-off valve that opens only upon insertion of the correct oxygen probe. Terminal units shall be manufactured from materials compatible with 100% oxygen service, cleaned and degreased for oxygen use, and fitted with permanent gas identification. Oxygen terminal units shall be compliant with HTM 02-01, NFPA 99, and applicable ISO standards and shall not permit cross- connection with other medical gases
| oxygen terminals(wall mounted)(BS type) | No | 16 |  | 0
B)Medical Air Terminal Units
Supply,Installation, testing and commissioning of Medical Air terminal units shall be designed for connection to a 400 kPa (MA4) medical air pipeline system and shall incorporate an automatic self-sealing valve actuated only by the correct medical air probe. Terminal units shall be manufactured from corrosion-resistant materials, suitable for oil-free medical air service, and permanently identified for medical air. Medical air terminal units shall comply with HTM 02-01, NFPA 99, and EN ISO 7396-1 requirements and shall be compatible with neonatal respiratory equipment and air–oxygen blenders.
| Medical Air terminals(wall mounted)(BS type) | No | 16 |  | 0
C)Medical GAS Terminal Probe Units
Supply and installation of medical gas terminal units for Oxygen and Medical Air complete with BS standard gas-specific probes, non- interchangeable indexing system, self-sealing mechanism, and all necessary accessories, fully compliant with HTM 02-01, ISO 7396-1, and EN ISO 9170-1.
| Medical air Probe | No | 20 |  | 0
| Oxygen Probe | No | 20 |  | 0
1.12 | TRUNKING
Supply Install medical trunking system as shown on the drawing complete with all fixing acessories. The unit must fulfill HTM 2022 requirements.
| Color: as per the client approval | ml | 145 |  | 0
1.13 | OXYGEN MANIFOLD RELOCATION AND INTEGRATION WORKS
| Dismantling, relocation, reinstallation, connection, testing, and commissioning of existing oxygen manifold system (2 × 4 cylinder configuration), including all required piping, fittings, regulators, and accessories, fully integrated with the new MGPS system and compliant with HTM 02-01, ISO 7396-1, and NFPA 99. | No | 1 |  | 0
1.14 | MEDICAL AIR PLANT RELOCATION AND INTEGRATION WORKS
| Dismantling, relocation, reinstallation, connection, testing, and commissioning of existing Medical air system including all required piping, fittings, regulators, and accessories, fully integrated with the new MGPS system and compliant with HTM 02-01, ISO 7396-1, and NFPA 99. | No | 1 |  | 0
1.15 | MGPS PLANT ROOM LIGHTWEIGHT ACOUSTIC ENCLOSURE AND ASSOCIATED WORKS Note: This intervention subjected for prior approval and the actual location will be defined during the site visit.
Supply, install, test, and complete all works necessary to provide a fully functional MGPS plant room enclosure room size 3.3mx6.6m, including construction of new lightweight partition walls, access door, sealing, ventilation, and basic vibration isolation measures, as required to achieve a technically suitable and cost-effective installation.
Scope of Works shall include, but not be limited to, the following:
Acoustic Lightweight Partition Walls
Construction of standard lightweight partition walls to the MGPS plant room (two new walls only), comprising galvanized steel stud framing (minimum 75 mm depth), single layer of 12.5 mm gypsum boards to each side, and mineral wool infill insulation (minimum 50 mm thickness), including full-height installation from slab to slab, jointing, finishing, and all necessary fixings.The wall assembly shall provide basic sound attenuation suitable for plant room applications but shall not be designed as a high-performance acoustic enclosure.
Acoustic and Fire-Rated Sealing
Provision of sealant to all wall perimeters, junctions, and service penetrations (pipes, conduits, cable trays), ensuring adequate airtightness and proper finishing.
Plant Room Access Door
Supply and installation of a standard steel or solid-core access door to the MGPS plant room, complete with frame, basic perimeter rubber seals, heavy- duty hinges, door closer, and lockset.Door shall be labeled: “MGPS PLANT ROOM – AUTHORIZED PERSONNEL ONLY” Door frame and interfaces shall be properly sealed to surrounding construction.
Ventilation System
Provision of plant room ventilation comprising: Window-mounted fresh air fan, minimum capacity 800 ms/hr, complete with mounting frame, bird screen, and accessories Window-mounted exhaust fan, minimum capacity 900 ms/hr, complete with backdraft shutter and mounting accessories All openings shall be properly finished and sealed to the wall construction. No specialized acoustic duct lining or plenum boxes are included in this simplified configuration.
Basic Vibration Isolation
Provision and installation of basic vibration isolation measures for MGPS mechanical equipment, including: >elastomeric pads or mounts under equipment >flexible pipe connections where required to reduce transmission of vibration to the structure.
Electrical and Lighting Works
Completion of all finishing works including: >surface preparation and painting of partition walls >sealing of joints and edges >cleaning and snagging to deliver a neat and functional plant room.
Coordination, Testing, and Completion
| Full coordination with mechanical, electrical, and fire protection services; completion of all associated builder’s works; reinstatement of finishes; and delivery of a complete, operational MGPS plant room enclosure meeting the acoustic and functional requirements of the project. | LPS | 1 |  | 0
Note: The scope includes provision of power supply using appropriate components, including power cables and a control panel (if required), from the nearest suitable location, as well as connection to the nearest earthing loop. Any damage to walls, floors, or other components resulting from these works shall be repaired using the same materials to restore the affected areas to their original condition.

## Table 3 (hidden)
Supply, Installation, testing and commisioning of medical gas Master alarm service module. The unit is supplied as a complete package, fully tested prior to shipping. The unit equipped with stamped gas identification shut-off valve (100% leakage free) stainless steel back plate, box, clear emergency glass panel, local area alarm, pressure switch, indication light, acess panel internal battery and fully integrated control. The unit shall be used for all medical gases and vacuum as shown and specified on the drawing.
| MASTER ALARM ( FOR 3GASES ) | No | 1 | 1500 | 1500
1.9 | PIPE WORK
Supply,Install oxy/med copper pipe as shown on the drawing complete with all fittings, valves,sealant,support hanger and all accessories to make the system functional. Copper tubing used for medical gas and vacuum pipeline systems (oxygen, medical air, and vacuum) shall be seamless, medical-grade copper manufactured and certified in accordance with EN 13348. Tubing shall be supplied internally degreased, dried, and free from particulate contamination, suitable for oxygen service, and capped at both ends to prevent contamination during storage and installation. Copper pipes shall be installed strictly in accordance with HTM 02-01, NFPA 99, and the manufacturer’s recommendations, including requirements for cleanliness, jointing, pressure testing, and identification.
| Copper Pipe-Med, EN13348, ø12mm | Mt | 0 | 13.1 | -
| Copper Pipe-Med, EN13348, ø15mm | Mt | 104 | 18.4 | 1913.6
| Copper Pipe-Med, EN13348, ø22mm | Mt | 55 | 28.7 | 1578.5
| Copper Pipe-Med, EN13348, ø28mm | Mt | 82 | 35.4 | 2902.8
| Copper Pipe-Med, EN13348, ø35mm | Mt | 65 | 47.6 | 3094
1.1 | LINE VALVES
Supply and install Branch isolation valves serving oxygen, medical air, and vacuum pipeline branches, Valves shall be full-bore, quarter-turn ball valves specifically designed and certified for medical gas service. Valves shall be manufactured from dezincification-resistant brass or approved equivalent, be factory cleaned for oxygen service, and supplied capped to prevent contamination. Each branch isolation valve shall be fitted with a lockable operating handle to prevent inadvertent operation and shall be clearly labeled to identify the service gas and the area served. Installation of branch isolation valves shall comply with the requirements of HTM 02-01 and NFPA 99, ensuring accessibility for operation and maintenance
| Ball Valve Set, Chrome Plated, Male Conical Coupling - 12mm | No. | 9 | 16 | 144
| Ball Valve Set, Chrome Plated, Male Conical Coupling - 15mm | No. | 16 | 21.5 | 344
| Ball Valve Set, Chrome Plated, Male Conical Coupling - 22mm | No. | 20 | 29.4 | 588
| Ball Valve Set, Chrome Plated, Male Conical Coupling - 35mm | No. | 3 | 53 | 159
1.11 | Medical Gas Terminal Units
1.11.1 | Medical Gas Terminal Units with isolated arrangment
Medical gas terminal units shall be specifically designed for use in healthcare facilities and shall comply with HTM 02-01, NFPA 99, and EN ISO 7396-1 requirements. Terminal units shall be non-interchangeable between different gas services, incorporate an automatic self-sealing valve, and be suitable for the nominal pipeline operating pressure of the respective service. Terminal units shall be permanently gas-identified by color coding and clear labeling and shall be compatible with the medical gas outlet probe standard adopted for the facility
A)Oxygen Terminal Units
Supply,Installation, testing and commissioning of Oxygen terminal units shall be designed for connection to a 400 kPa medical oxygen pipeline system and shall incorporate an automatic shut-off valve that opens only upon insertion of the correct oxygen probe. Terminal units shall be manufactured from materials compatible with 100% oxygen service, cleaned and degreased for oxygen use, and fitted with permanent gas identification. Oxygen terminal units shall be compliant with HTM 02-01, NFPA 99, and applicable ISO standards and shall not permit cross- connection with other medical gases
| oxygen terminals(wall mounted)(BS type) | No | 16 | 72 | 1152
B)Medical Air Terminal Units
Supply,Installation, testing and commissioning of Medical Air terminal units shall be designed for connection to a 400 kPa (MA4) medical air pipeline system and shall incorporate an automatic self-sealing valve actuated only by the correct medical air probe. Terminal units shall be manufactured from corrosion-resistant materials, suitable for oil-free medical air service, and permanently identified for medical air. Medical air terminal units shall comply with HTM 02-01, NFPA 99, and EN ISO 7396-1 requirements and shall be compatible with neonatal respiratory equipment and air–oxygen blenders.
| Medical Air terminals(wall mounted)(BS type) | No | 16 | 72 | 1152
C)Medical GAS Terminal Probe Units
Supply and installation of medical gas terminal units for Oxygen and Medical Air complete with BS standard gas-specific probes, non- interchangeable indexing system, self-sealing mechanism, and all necessary accessories, fully compliant with HTM 02-01, ISO 7396-1, and EN ISO 9170-1.
| Medical air Probe | No | 20 | 25 | 500
| Oxygen Probe | No | 20 | 25 | 500
1.12 | TRUNKING
Supply Install medical trunking system as shown on the drawing complete with all fixing acessories. The unit must fulfill HTM 2022 requirements.
| Color: as per the client approval | ml | 145 | 120 | 17400
1.15 | OXYGEN MANIFOLD RELOCATION AND INTEGRATION WORKS
| Dismantling, relocation, reinstallation, connection, testing, and commissioning of existing oxygen manifold system (2 × 4 cylinder configuration), including all required piping, fittings, regulators, and accessories, fully integrated with the new MGPS system and compliant with HTM 02-01, ISO 7396-1, and NFPA 99. | No | 1 | 1600 | 1600
1.15 | MEDICAL AIR PLANT RELOCATION AND INTEGRATION WORKS
| Dismantling, relocation, reinstallation, connection, testing, and commissioning of existing Medical air system including all required piping, fittings, regulators, and accessories, fully integrated with the new MGPS system and compliant with HTM 02-01, ISO 7396-1, and NFPA 99. | No | 1 | 1940 | 1940
1.16 | MGPS PLANT ROOM LIGHTWEIGHT ACOUSTIC ENCLOSURE AND ASSOCIATED WORKS
Supply, install, test, and complete all works necessary to provide a fully functional MGPS plant room enclosure room size 3.3mx6.6m, including construction of new lightweight partition walls, access door, sealing, ventilation, and basic vibration isolation measures, as required to achieve a technically suitable and cost-effective installation.
Scope of Works shall include, but not be limited to, the following:
Acoustic Lightweight Partition Walls
Construction of standard lightweight partition walls to the MGPS plant room (two new walls only), comprising galvanized steel stud framing (minimum 75 mm depth), single layer of 12.5 mm gypsum boards to each side, and mineral wool infill insulation (minimum 50 mm thickness), including full-height installation from slab to slab, jointing, finishing, and all necessary fixings.The wall assembly shall provide basic sound attenuation suitable for plant room applications but shall not be designed as a high-performance acoustic enclosure.
Acoustic and Fire-Rated Sealing
Provision of sealant to all wall perimeters, junctions, and service penetrations (pipes, conduits, cable trays), ensuring adequate airtightness and proper finishing.
Plant Room Access Door
Supply and installation of a standard steel or solid-core access door to the MGPS plant room, complete with frame, basic perimeter rubber seals, heavy- duty hinges, door closer, and lockset.Door shall be labeled: “MGPS PLANT ROOM – AUTHORIZED PERSONNEL ONLY” Door frame and interfaces shall be properly sealed to surrounding construction.
Ventilation System
Provision of plant room ventilation comprising: Window-mounted fresh air fan, minimum capacity 800 ms/hr, complete with mounting frame, bird screen, and accessories Window-mounted exhaust fan, minimum capacity 900 ms/hr, complete with backdraft shutter and mounting accessories All openings shall be properly finished and sealed to the wall construction. No specialized acoustic duct lining or plenum boxes are included in this simplified configuration.
Basic Vibration Isolation
Provision and installation of basic vibration isolation measures for MGPS mechanical equipment, including: >elastomeric pads or mounts under equipment >flexible pipe connections where required to reduce transmission of vibration to the structure.
Electrical and Lighting Works
Completion of all finishing works including: >surface preparation and painting of partition walls >sealing of joints and edges >cleaning and snagging to deliver a neat and functional plant room.
Coordination, Testing, and Completion
| Full coordination with mechanical, electrical, and fire protection services; completion of all associated builder’s works; reinstatement of finishes; and delivery of a complete, operational MGPS plant room enclosure meeting the acoustic and functional requirements of the project. | LPS | 1 | 8500 | 8500